Образец перевода с русского языка на английский – инструкция по эксплуатации котла

This instruction is intended for maintenance staff of operated boilers.

Instruction for use consists of the following parts:

- Description and operation of the boiler is its units;

- List of technological protections and blockings;

- Use according to its intended purpose; maintenance;

4.   Basic requirements for fail-safe functioning and secure maintenance of the boiler.

……………………………..

Feed water, supplied into the boiler, passes through a water economizer, heats up to the temperature close to saturation temperature, and goes to the boiler drum, from where it is directed to the lower chambers of evaporating shields of the furnace.  From the upper chambers of furnace shields, the steam-water mixture is directed to the boiler drum, thus the boiler natural circulation takes place.

The steam-water mixture is separated in the drum, and the saturated steam goes from the drum to the steam superheater, and the water – to the water zone of the boiler, there mixes together with incoming feed water and again goes to the evaporating shields of the furnace.

…………………………….

Ceiling steam superheater (picture 1.6) consists of 4 inlet collectors 219x26 mm in diameter, to which the pipes from ceiling shields 32x5 mm in diameter are connected, 40 pipes in each panel with interval of 52 mm. Each collector receives steam directly from the boiler drum through two pipes 133x13 mm in diameter.

…………………………….

3.1.	The pollution level of internal surfaces of the boiler water-steam duct must not be over 50g/sqm, when the boiler is put into operation. To achieve the required cleanness after the boiler installation, the water-steam duct, main pipelines and feeding duct elements must be washed with water-chemical solution, and their cleanness must be controlled.

3.2.	After installation the boiler must not be started and, after heating surfaces repair the boiler must not be run without prior hydraulic testing. The testing should be carried out with water of above-zero temperature between +5°С and +40°С and testing pressure level equal to 1,25 of operation pressure in the boiler drum. Pressure level increase time must be no less than 10 minutes.

3.3.	The boiler emergency valves should be set to the operation pressure equal to 1,1 of the specified. The valves are set up during the process of the boiler steam testing and steam pipelines blowing before the boiler starts.

…………………………