| Оригинал (англ) | Перевод (русс) |
| --- | --- |
| Instructions for correct refrigerant installation _ The execution of refrigerant lines for connection with the evaporator section must be properly performed by the client in compliance with current laws. It is especially advisable to refer to standard EN 378-2 and subsequent modifications. _ The refrigerant lines must be in copper piping for refrigeration systems, type EN 12735-1-2, electrolytic, mild copper, degreased, and de-oxidised. Make sure there are no impurities or moisture inside the pipes as this is extremely harmful for the refrigerant circuit. _ It is advisable to insulate the liquid line in cases where the external temperature (because of solar radiation) is higher than the temperature of the liquid itself. _ It is advisable to insulate the gas line to avoid burns from accidental contact, or to avoid heating indoor areas. _ Properly size the refrigerant lines so as to obtain limited leaks and a speed of the refrigerant liquid that guarantees carrying of the oil. _ The diameters of the inlet/outlet pipes of the remote condensers are shown in the table of dimensional characteristics on page 7. The table below shows the recommended dimensions for the refrigerant connection between the remote condenser and the evaporator unit, based on equivalent length. _ It is advisable to install, between the evaporator and the remote condenser, an anti-vibration device (1) and a silencer (2) so as to reduce the transmission of noise along the ducting (fig. 10). _ Horizontal stretches of pipe should end up sloping gently towards the low point (in the sense of gas flow), to favour the flow of oil. The slope should be between 0.5% and 1%. | Инструкция по установке хладагента Покупатель должен осуществлять подключение линии подачи хладагента к испарителю в соответствии со всеми техническими нормами. В особенно это касается холодильных систем стандарта EN 378-2 и последующих модификаций. Линии подачи хладагента должны быть изготовлены из медных трубок, выполненных из электролитической мягкой обезжиренной раскисленной меди марки EN 12735-1-2. Убедитесь в том, что внутри линий нет загрязнений или влажности, так как это может нанести вред контуру хладагента. Рекомендуется изолировать жидкостный трубопровод в случае если наружная температура превышает (например, из-за солнечного излучения) температуру самой жидкости. Во избежание возгораний, которые могут быть вызваны случайными соприкосновениями или перегрева окружающего пространства, рекомендуется и изоляция газового трубопровода. Размер линий подачи важен для того, чтобы минимизировать протечки и обеспечить транспортировку нефти. Диаметры впускной и выпускной труб вынесенного кондиционера указаны в таблице геометрических характеристик на странице 7. В нижеприведённой таблице указаны основанные на принципе эквивалентной длины рекомендуемые геометрические характеристики для соединения вынесенного кондиционера хладагента и испарительного агрегата. Для минимизирования пропускания шумов в трубопровод (10), рекомендуется установить виброгаситель (1) и глушитель шума (2). Горизонтальные поверхности к концу трубопровода должны быть слегка по направлению к нижней точке (относительно потока газа), что способствует движению потока нефти. Уклон варьируется от 0.5% до 1% |

| ХХХ is a reverse osmosis filtration unit with spiral wound membranes designed for continuous concentration of whey or milk before further processing. The membrane separates the feed into two streams: retentate and permeate. The process sequences of the XXX unit can be divided into following main steps: start up, water circulation, pre-concentration, production, emptying, rinse, and Cleaning-In-Place (CIP). The reverse osmosis membrane allows water to pass through it during the concentration process and at the same time the membrane retains solids in the feed. In this way the dissolved salts, lactose, acids, proteins, fat and bacteria are concentrated in the retentate. The unit is fully controlled from a Human Machine Interface (HMI) via a touch screen. The HMI is used for monitoring the unit, activation of functions, setting of parameters and alarm handling. During processing the XXX unit only requires regular surveillance of process values. The control system includes essential process alarms for protection of the equipment. | ХХХ представляет собой блок для проведения обратного осмоса, оборудованный спирально-намотанными мембранными элементами, предназначенными для непрерывного сгущения сыворотки или молока перед последующими этапами обработки. Мембрана разделяет подаваемый продукт на два потока: ретентат и пермеат. Последовательность операций, выполняемых ХХХ, выглядит следующим образом: запуск, промывка водой, предварительное сгущение, производство, опорожнение, промывка и безразборная мойка (CIP). Мембрана для обратного осмоса пропускает воду и одновременно аккумулирует твёрдые частицы, содержащиеся в подаваемом материале. Таким образом, растворённые соли, лактоза, кислоты, белки, жиры и бактерии и аккумулируются в ретентате. Управление прибором осуществляется с помощью человеко-машинного интерфейса (HMI) в виде экрана с сенсорным управлением. ЧМИ применяется для управления прибором, запуска операций, ввода параметров и обработки сигналов тревоги. Во время процесса переработки блок ХХХ требует лишь регулярного наблюдения. Система контроля над прибором содержит аварийную сигнализацию для предотвращения повреждения оборудования. |
| --- | --- |

| Переводчик: | Боровикова Ульяна Викторовна © |
| --- | --- |